## Instructions
Giardia and Virus Profile Spreadsheet
This spreadsheet will automatically calculate Giardia and virus inactivation/removal through the disinfection process. Begin by determining which segments of your water treatment plant will be used in the profile. Gather information for these segments (up to nine spaces are provided) and fill out the "Segments" sheet with the necessary information. Any segment not used should show "Not In Use" under the Treatment Segment. Fill out all all the required information for each segment. Next gather information each day for each segment during the peak hourly flow through your water treatment plant and fill out the "Calculation Page". Once the required data is entered you can view the data easily on the "Month Summary" sheet or on the "Month Graph" sheet. Submit Reports To: ADEM - Drinking Water Branch Post Office Box 301463 Montgomery, Alabama 36130-1463 References: EPA's ct_chlorine.xls spreadhseet EPA's Handbook: Optmizing Water Treatment Plant Performance Using The Composite Correction Program (1998 edition) Surface Water Treatment Rule
Version | 1.1
Created | 2003-09-09
Modified | 2003-09-22
Clear Calculation Page
(WARNING ALL DATA WILL BE LOST IF NOT SAVED)

## Segments
[7 empty] | Segment | Oxidant | Baffling | Basin Type
| Treatment Segment | Disinfectant | Baffling Factor | Basin Type | Basin Dimensions |  | Not In Use | None | 0 | Circular
Segment 1 | Rapid Mix | Chlorine | 1 | Rectangular |  |  | Rapid Mix | Chlorine | 0.1 | Rectangular
[5 empty] | Height (ft) |  | Flocculation | Chloramines | 0.3
[5 empty] | Width (ft) | 6.75 | Sedimentation | Chlorine Dioxide | 0.5
| Area (Gal) | 366.0525 |  |  | Length (ft) | 7.25 | Filtration | Ozone | 0.7
| Remove Area (Gal) | 0 |  |  |  |  | Clearwell |  | 0.9
[7 empty] | Pipe |  | 1
| Treatment Segment | Disinfectant | Baffling Factor | Basin Type | Basin Dimensions
Segment 2 | Flocculation | Chlorine | 0.7 | Rectangular
Height (ft)
Width (ft)
| Area (Gal) | 0 |  |  | Length (ft)
| Remove Area (Gal) | 0
| Treatment Segment | Disinfectant | Baffling Factor | Basin Type | Basin Dimensions
Segment 3 | Sedimentation | Chlorine | 0.3 | Rectangular
Height (ft)
Width (ft)
| Area (Gal) | 0 |  |  | Length (ft)
| Remove Area (Gal) | 0
| Treatment Segment | Disinfectant | Baffling Factor | Basin Type | Basin Dimensions
Segment 4 | Filtration | Chlorine | 0.5 | Rectangular
Height (ft)
[5 empty] | Width (ft) | 34
| Area (Gal) | 2733.94 |  |  | Length (ft) | 21.5
| Remove Area (Gal) | 0
Media Volume (Gal)
Gravel Volume (Gal)
Underdrain Volume (Gal)
| Treatment Segment | Disinfectant | Baffling Factor | Basin Type | Basin Dimensions
Segment 5 | Clearwell | Chlorine | 0.1 | Rectangular
[5 empty] | Height (ft) | 10
[5 empty] | Width (ft) | 130
| Area (Gal) | 9918.48 |  |  | Length (ft) | 102
| Remove Area (Gal) | 0
| Treatment Segment | Disinfectant | Baffling Factor | Basin Type | Basin Dimensions
Segment 6 | Not In Use | None | 1 | Circular
Height (ft)
Diameter (ft)
| Area (Gal) | 0
| Remove Area (Gal) | 0
| Treatment Segment | Disinfectant | Baffling Factor | Basin Type | Basin Dimensions
Segment 7 | Not In Use | None | 1 | Circular
Height (ft)
Diameter (ft)
| Area (Gal) | 0
| Remove Area (Gal) | 0
| Treatment Segment | Disinfectant | Baffling Factor | Basin Type | Basin Dimensions
Segment 8 | Not In Use | None | 1 | Circular
Height (ft)
Diameter (ft)
| Area (Gal) | 0
| Remove Area (Gal) | 0
| Treatment Segment | Disinfectant | Baffling Factor | Basin Type | Basin Dimensions
Segment 9 | Not In Use | None | 1 | Circular
Height (ft)
Diameter (ft)
| Area (Gal) | 0
| Remove Area (Gal) | 0
Note on E4: Baffling Conditions Efficiency Baffling Description ------------------------------------------------------------------------------------------------------------ Unbaffled 0.1 None; Agitated basin, high inlet and outlet flow velocities; variable water level Poor 0.3 Single or multiple unbaffled inlets and outlets, no intra-basin baffles Average 0.5 Baffled inlet or outlet with some intra- basin baffling Superior 0.7 Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated weir Excellent 0.9 Serpentine baffling throughout basin Perfect (plug flow) 1.0 Pipeline flow
Note on E15: Baffling Conditions Efficiency Baffling Description ------------------------------------------------------------------------------------------------------------ Unbaffled 0.1 None; Agitated basin, high inlet and outlet flow velocities; variable water level Poor 0.3 Single or multiple unbaffled inlets and outlets, no intra-basin baffles Average 0.5 Baffled inlet or outlet with some intra- basin baffling Superior 0.7 Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated weir Excellent 0.9 Serpentine baffling throughout basin Perfect (plug flow) 1.0 Pipeline flow
Note on E26: Baffling Conditions Efficiency Baffling Description ------------------------------------------------------------------------------------------------------------ Unbaffled 0.1 None; Agitated basin, high inlet and outlet flow velocities; variable water level Poor 0.3 Single or multiple unbaffled inlets and outlets, no intra-basin baffles Average 0.5 Baffled inlet or outlet with some intra- basin baffling Superior 0.7 Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated weir Excellent 0.9 Serpentine baffling throughout basin Perfect (plug flow) 1.0 Pipeline flow
Note on E39: Baffling Conditions Efficiency Baffling Description ------------------------------------------------------------------------------------------------------------ Unbaffled 0.1 None; Agitated basin, high inlet and outlet flow velocities; variable water level Poor 0.3 Single or multiple unbaffled inlets and outlets, no intra-basin baffles Average 0.5 Baffled inlet or outlet with some intra- basin baffling Superior 0.7 Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated weir Excellent 0.9 Serpentine baffling throughout basin Perfect (plug flow) 1.0 Pipeline flow
Note on E50: Baffling Conditions Efficiency Baffling Description ------------------------------------------------------------------------------------------------------------ Unbaffled 0.1 None; Agitated basin, high inlet and outlet flow velocities; variable water level Poor 0.3 Single or multiple unbaffled inlets and outlets, no intra-basin baffles Average 0.5 Baffled inlet or outlet with some intra- basin baffling Superior 0.7 Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated weir Excellent 0.9 Serpentine baffling throughout basin Perfect (plug flow) 1.0 Pipeline flow
Note on E61: Baffling Conditions Efficiency Baffling Description ------------------------------------------------------------------------------------------------------------ Unbaffled 0.1 None; Agitated basin, high inlet and outlet flow velocities; variable water level Poor 0.3 Single or multiple unbaffled inlets and outlets, no intra-basin baffles Average 0.5 Baffled inlet or outlet with some intra- basin baffling Superior 0.7 Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated weir Excellent 0.9 Serpentine baffling throughout basin Perfect (plug flow) 1.0 Pipeline flow
Note on E74: Baffling Conditions Efficiency Baffling Description ------------------------------------------------------------------------------------------------------------ Unbaffled 0.1 None; Agitated basin, high inlet and outlet flow velocities; variable water level Poor 0.3 Single or multiple unbaffled inlets and outlets, no intra-basin baffles Average 0.5 Baffled inlet or outlet with some intra- basin baffling Superior 0.7 Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated weir Excellent 0.9 Serpentine baffling throughout basin Perfect (plug flow) 1.0 Pipeline flow
Note on E85: Baffling Conditions Efficiency Baffling Description ------------------------------------------------------------------------------------------------------------ Unbaffled 0.1 None; Agitated basin, high inlet and outlet flow velocities; variable water level Poor 0.3 Single or multiple unbaffled inlets and outlets, no intra-basin baffles Average 0.5 Baffled inlet or outlet with some intra- basin baffling Superior 0.7 Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated weir Excellent 0.9 Serpentine baffling throughout basin Perfect (plug flow) 1.0 Pipeline flow
Note on E96: Baffling Conditions Efficiency Baffling Description ------------------------------------------------------------------------------------------------------------ Unbaffled 0.1 None; Agitated basin, high inlet and outlet flow velocities; variable water level Poor 0.3 Single or multiple unbaffled inlets and outlets, no intra-basin baffles Average 0.5 Baffled inlet or outlet with some intra- basin baffling Superior 0.7 Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated weir Excellent 0.9 Serpentine baffling throughout basin Perfect (plug flow) 1.0 Pipeline flow

## Calculation Page
Day 1 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 7 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 25 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 29 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944 |  | Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944 |  | Rapid Mix | 1400 | 10 | 1.5 | 7.5 | 15 | 3660.525 | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527 |  | Rapid Mix | 1400 | 10 | 1.5 | 7.5 | 15 | 3660.525 | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527
| Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 |  | 1.4 | 7.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 |  | 1.4 | 7.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0
| Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392 |  | Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586 |  | Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714 |  | Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714 |  | Total For Day | [6 empty] | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527 |  | Total For Day | [6 empty] | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527
Day 2 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 8 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 26 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 30 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944 |  | Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944 |  | Rapid Mix | 1400 | 10 | 1.5 | 7.5 | 15 | 3660.525 | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527 |  | Rapid Mix | 1400 | 10 | 1.5 | 7.5 | 15 | 3660.525 | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527
| Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 |  | 1.4 | 7.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 |  | 1.4 | 7.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0
| Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392 |  | Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586 |  | Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714 |  | Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714 |  | Total For Day | [6 empty] | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527 |  | Total For Day | [6 empty] | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527
Day 3 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 9 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 27 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 31 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944 |  | Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944 |  | Rapid Mix | 1400 | 10 | 1.5 | 7.5 | 15 | 3660.525 | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527 |  | Rapid Mix | 1400 | 10 | 1.5 | 7.5 | 15 | 3660.525 | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527
| Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 |  | 1.4 | 7.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 |  | 1.4 | 7.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0
| Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392 |  | Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586 |  | Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714 |  | Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714 |  | Total For Day | [6 empty] | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527 |  | Total For Day | [6 empty] | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527
Day 4 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 10 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 28 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944 |  | Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944 |  | Rapid Mix | 1400 | 10 | 1.5 | 7.5 | 15 | 3660.525 | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527
| Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 |  | 1.4 | 7.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0
| Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392 |  | Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586 |  | Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714 |  | Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714 |  | Total For Day | [6 empty] | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527
Day 5 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 11 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944 |  | Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944
| Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0
| Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0
| Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392 |  | Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392
| Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586 |  | Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714 |  | Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714
Day 6 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 12 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944 |  | Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944
| Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0
| Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0
| Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392 |  | Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392
| Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586 |  | Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714 |  | Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714
Day 13 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 19 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944 |  | Rapid Mix | 1400 | 9 | 1.4 | 7.4 | 14 | 3294.4725 | 3.2945 | 2.8849 | 0.09489 | 0.72124 | 0.03163
| Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 |  | 1.4 | 7.4 | 14 | 0 | 0 | 0 | 0 | 0 | 0
| Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714 |  | Total For Day | [6 empty] | 3.2945 | 2.8849 | 0.09489 | 0.72124 | 0.03163
Day 14 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 20 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| Rapid Mix | 1400 | 12 | 0.3 | 6.9 | 19 | 4392.63 | 0.94128 | 1.0909 | 0.058321 | 0.27273 | 0.01944 |  | Rapid Mix | 1600 | 11 | 1.55 | 7.5 | 15 | 4026.5775 | 3.9007 | 3.7059 | 0.11439 | 0.92648 | 0.03813
| Flocculation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1600 |  | 1.5 | 7.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0
| Sedimentation | 1400 | 12 | 0 | 6.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Filtration | 1400 | 5 | 0.5 | 6.9 | 19 | 13669.7 | 4.882 | 6.2562 | 0.28017 | 1.5641 | 0.093392 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Clearwell | 1400 | 10 | 1.5 | 7 | 19 | 99184.8 | 106.2694 | 139.1485 | 4.9757 | 34.7871 | 1.6586 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total For Day | [6 empty] | 112.0927 | 146.4957 | 5.3142 | 36.6239 | 1.7714 |  | Total For Day | [6 empty] | 3.9007 | 3.7059 | 0.11439 | 0.92648 | 0.03813
Day 15 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 21 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| Rapid Mix | 1400 | 10 | 1.5 | 7.5 | 15 | 3660.525 | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527 |  | Rapid Mix | 800 | 12 | 1.4 | 7.5 | 10 | 4392.63 | 7.6871 | 5.1753 | 0.16182 | 1.2938 | 0.053941
| Flocculation | 1400 |  | 1.4 | 7.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 800 |  | 1.35 | 7.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0
| Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total For Day | [6 empty] | 3.922 | 3.7269 | 0.11558 | 0.93172 | 0.038527 |  | Total For Day | [6 empty] | 7.6871 | 5.1753 | 0.16182 | 1.2938 | 0.053941
Day 16 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 22 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| Rapid Mix | 1400 | 9.5 | 1.4 | 7.8 | 17 | 3477.4988 | 3.4775 | 3.8118 | 0.10704 | 0.95296 | 0.035681 |  | Rapid Mix | 1400 | 12 | 1.5 | 7.5 | 15 | 4392.63 | 4.7064 | 4.5008 | 0.1387 | 1.1252 | 0.046232
| Flocculation | 1400 |  | 1.4 | 7.8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 |  | 1.4 | 7.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0
| Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total For Day | [6 empty] | 3.4775 | 3.8118 | 0.10704 | 0.95296 | 0.035681 |  | Total For Day | [6 empty] | 4.7064 | 4.5008 | 0.1387 | 1.1252 | 0.046232
Day 17 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 23 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| Rapid Mix | 1600 | 11 | 1.6 | 7.5 | 16 | 4026.5775 | 4.0266 | 4.1224 | 0.12596 | 1.0306 | 0.041986 |  | Rapid Mix | 1400 | 7 | 1.5 | 7.2 | 15 | 2562.3675 | 2.7454 | 2.566 | 0.090296 | 0.64149 | 0.030099
| Flocculation | 1600 |  | 1.6 | 7.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 |  | 1.4 | 7.2 | 15 | 0 | 0 | 0 | 0 | 0 | 0
| Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total For Day | [6 empty] | 4.0266 | 4.1224 | 0.12596 | 1.0306 | 0.041986 |  | Total For Day | [6 empty] | 2.7454 | 2.566 | 0.090296 | 0.64149 | 0.030099
Day 18 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio | Day 24 | Segment | Peak Flow Rate (gpm) | Water Depth (ft) | Residual mg/L | pH | Temp ° C | Effective Volume | Actual CT | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| Rapid Mix | 1200 | 12 | 1.3 | 7 | 14 | 4392.63 | 4.7587 | 4.2306 | 0.16094 | 1.0577 | 0.053647 |  | Rapid Mix | 1400 | 10 | 1.5 | 7.3 | 15 | 3660.525 | 3.922 | 3.7269 | 0.1243 | 0.93172 | 0.041432
| Flocculation | 1200 |  | 1.2 | 7 | 14 | 0 | 0 | 0 | 0 | 0 | 0 |  | Flocculation | 1400 |  | 1.4 | 7.3 | 15 | 0 | 0 | 0 | 0 | 0 | 0
| Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Sedimentation | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Filtration | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Clearwell | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | Not In Use | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total For Day | [6 empty] | 4.7587 | 4.2306 | 0.16094 | 1.0577 | 0.053647 |  | Total For Day | [6 empty] | 3.922 | 3.7269 | 0.1243 | 0.93172 | 0.041432

## Month Summary
Giardia and Virus Monthly Profile Summary
| System Name | System Name
| PWSID | AL5555555
| Plant Name | Water Treatment Plant Name
| Month & Year | 2003-09-01
John J. Doe
Prepared By
| Day | Virus Log Removal | Giardia Log Removal | Virus Inactivation Ratio | Giardia Inactivation Ratio
| 1 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 2 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 3 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 4 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 5 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 6 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 7 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 8 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 9 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 10 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 11 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 12 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 13 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 14 | 146.4957 | 5.3142 | 36.6239 | 1.7714
| 15 | 3.7269 | 0.11558 | 0.93172 | 0.038527
| 16 | 3.8118 | 0.10704 | 0.95296 | 0.035681
| 17 | 4.1224 | 0.12596 | 1.0306 | 0.041986
| 18 | 4.2306 | 0.16094 | 1.0577 | 0.053647
| 19 | 2.8849 | 0.09489 | 0.72124 | 0.03163
| 20 | 3.7059 | 0.11439 | 0.92648 | 0.03813
| 21 | 5.1753 | 0.16182 | 1.2938 | 0.053941
| 22 | 4.5008 | 0.1387 | 1.1252 | 0.046232
| 23 | 2.566 | 0.090296 | 0.64149 | 0.030099
| 24 | 3.7269 | 0.1243 | 0.93172 | 0.041432
| 25 | 3.7269 | 0.11558 | 0.93172 | 0.038527
| 26 | 3.7269 | 0.11558 | 0.93172 | 0.038527
| 27 | 3.7269 | 0.11558 | 0.93172 | 0.038527
| 28 | 3.7269 | 0.11558 | 0.93172 | 0.038527
| 29 | 3.7269 | 0.11558 | 0.93172 | 0.038527
| 30 | 3.7269 | 0.11558 | 0.93172 | 0.038527
| 31 | 3.7269 | 0.11558 | 0.93172 | 0.038527
| Maximum | 146.4957 | 5.3142 | 36.6239 | 1.7714
| Average | 68.2413 | 2.4659 | 17.0603 | 0.82196
| Minimum | 2.566 | 0.090296 | 0.64149 | 0.030099

## Month Graph
System Name | System Name
PWSID | AL5555555
Plant Name | Water Treatment Plant Name
Month & Year | 2003-09-01
Prepared By